|  | Engine 526cc Tohatsu 4-stroke,3-cylinder, water cooled gasoline engine Authorized output 30PS (22kW) Pump performance 1200 liter / min. at 0.6MPa 950 liter / min. at 0.8MPa 700 liter / min. at 1.0MPa Dry weight 101kg |
| --- | --- |

## Features of VF53AS

1.Light weight and compact 
Engine and pump castings are made of anti corrosive aluminum-alloy to reduce weight and prolong 
working life.

2.Maximum reliability 
VF53AS is powered by TOHATSU's original developed 4stroke 3cylinder engine which has achieved
lower emission and maximum fuel economy for environment protection. The technology which has 
proved itself in TOHATSU's state-of-the-art outboard engines ensures maximum reliability for any fire 
fighting scenes in all seasonal condition.

3.Quick priming 
Quick priming is provided by simple operating Rotary Vane Vacuum Pump. The pump primes 3meters
in only 3seconds.

4.Low emission 
CO emission is lowered by 43%*. HC and NOx lowered by 90%*.

5.Low noise and less vibration 
Low noise (Reduced by 9dB*) and less vibration does not interfere with speech communication during
operation.
*Numerical data are comparison with our two stroke models operating at 0.4MPa.

6.Excellent fuel economy 
Electrically controlled fuel injection helps optimum fuel supply depending on engine speed,
maximizing lower fuel consumption.

7.Engine overheat protection sensor 
Engine overheat protection device is provided to safeguard against cooling water loss, and to protect 
engine in the operation with discharge valve closed. This device automatically shuts off engine when 
engine temperature reaches 80℃.

8.Electrically controlled fuel injection 
Electrically controlled fuel injection secures reliable engine starting under any weather condition even
in the event of low battery power.

9.Auto priming system 
Rotary vane vacuum pump is automatically activated after engine starts, and cut off once priming is completed.

10.Double swivel outlets rotating with in a 90 degree.

Accessories
1. Battery charger
2. Tool kit

Optional accessories
1.Floodlight projector
2.External fuel tank (stainless, 20liters)

Adapters
Some different type of adapters for suction inlet and discharge outlet are available.

| Tohatsu portable fire pump Model VF53AS Specifications |  |  |  |
| --- | --- | --- | --- |
| Model: |  | VF53AS |  |
| Engine: | Type: | Tohatsu 4-stroke, 3-cylinder, water cooled gasoline engine |  |
|  | Bore & Stroke: | 61mm x 60mm |  |
|  | Piston displacement: | 526cc |  |
|  | Authorized output: | 30PS (22kW) / 5800rpm |  |
|  | Fuel tank: | 10 liters |  |
|  | Fuel consumption: | 9.5 liters/h. |  |
|  | Ignition: | Flywheel magneto (Digital C.D.Ignition) |  |
|  | Starting system: | Starter motor and automatic recoil system |  |
|  | Lubrication: | Wet sump |  |
|  | Engine oil: | API rating of SF, SG, SH or SJ. SAE 10W30/40 |  |
|  | Engine oil tank capacity: | 2 liter (when oil filter is replaced) |  |
|  | Spark plug: | NGK DCPR6E |  |
|  | Floodlight projector: | 12V55W |  |
|  | Battery: | 12V-16Ah/ 5h |  |
| Pump: | Type: | Single suction, single stage, high pressure turbine pump |  |
|  | Discharge outlet coupling: | JIS fire thread (B-9912) 2-1/2" (65mm) male |  |
|  |  | BSP 65mm (G2-1/2") male |  |
|  | Suction inlet coupling: | JIS fire thread (B-9912) 3" (75mm) male |  |
|  |  | BSP 100mm (G4") male |  |
|  | Priming: | Rotary-vane vacuum pump (Oilless type) |  |
| Pump performance: (Suction height: 3m) |  | 1200 liter/min. at 0.6MPa |  |
|  |  | 950 liter/min. at 0.8MPa |  |
|  |  | 700 liter/min. at 1.0MPa |  |
| Dimensions: |  | Length 670mm x Width 790mm x Height 740mm |  |
| Mass: | Dry: | 101kg |  |
|  | Wet: | 110kg |  |
| Max. suction height: |  | Approx. 9m (29.5 feet) |  |